## 控制命令说明
风机、灯光、水泵控制命令
设备通道1闭合：IRealTime.SetParm StaNo,903,"05","0000","65280"
设备通道1断开：IRealTime.SetParm StaNo,903,"05","0000","0"
设备通道2闭合：IRealTime.SetParm StaNo,903,"05","0001","65280"
设备通道2断开：IRealTime.SetParm StaNo,903,"05","0001","0"
设备通道3闭合：IRealTime.SetParm StaNo,903,"05","0002","65280"
设备通道3断开：IRealTime.SetParm StaNo,903,"05","0002","0"
设备通道4闭合：IRealTime.SetParm StaNo,903,"05","0003","65280"
设备通道4断开：IRealTime.SetParm StaNo,903,"05","0003","0"
空调控制命令 | 状态反馈
自动模式：IRealTime.SetParm StaNo,280,"05","0000","65280" | 自动模式：0
制冷20℃：IRealTime.SetParm StaNo,280,"05","0005","65280" | 制冷20℃：5
制冷21℃：IRealTime.SetParm StaNo,280,"05","0006","65280" | 制冷21℃：6
制冷22℃：IRealTime.SetParm StaNo,280,"05","0007","65280" | 制冷22℃：7
制冷23℃：IRealTime.SetParm StaNo,280,"05","0008","65280" | 制冷23℃：8
制冷24℃：IRealTime.SetParm StaNo,280,"05","0009","65280" | 制冷24℃：9
制冷25℃：IRealTime.SetParm StaNo,280,"05","0010","65280" | 制冷25℃：10
制冷26℃：IRealTime.SetParm StaNo,280,"05","0011","65280" | 制冷26℃：11
制冷27℃：IRealTime.SetParm StaNo,280,"05","0012","65280" | 制冷27℃：12
制冷28℃：IRealTime.SetParm StaNo,280,"05","0013","65280" | 制冷28℃：13
制冷29℃：IRealTime.SetParm StaNo,280,"05","0014","65280" | 制冷29℃：14
制冷30℃：IRealTime.SetParm StaNo,280,"05","0015","65280" | 制冷30℃：15
制热20℃：IRealTime.SetParm StaNo,280,"05","0020","65280" | 制热20℃：20
制热21℃：IRealTime.SetParm StaNo,280,"05","0021","65280" | 制热21℃：21
制热22℃：IRealTime.SetParm StaNo,280,"05","0022","65280" | 制热22℃：22
制热23℃：IRealTime.SetParm StaNo,280,"05","0023","65280" | 制热23℃：23
制热24℃：IRealTime.SetParm StaNo,280,"05","0024","65280" | 制热24℃：24
制热25℃：IRealTime.SetParm StaNo,280,"05","0025","65280" | 制热25℃：25
制热26℃：IRealTime.SetParm StaNo,280,"05","0026","65280" | 制热26℃：26
制热27℃：IRealTime.SetParm StaNo,280,"05","0027","65280" | 制热27℃：27
制热28℃：IRealTime.SetParm StaNo,280,"05","0028","65280" | 制热28℃：28
制热29℃：IRealTime.SetParm StaNo,280,"05","0029","65280" | 制热29℃：29
制热30℃：IRealTime.SetParm StaNo,280,"05","0030","65280" | 制热30℃：30
除湿：IRealTime.SetParm StaNo,280,"05","0031","65280" | 除湿：31
送风：IRealTime.SetParm StaNo,280,"05","0046","65280" | 送风：46
关机：IRealTime.SetParm StaNo,280,"05","0063","65280" | 关机：63